## County Plans
GridAid county plans: 5 urban and 5 rural counties
Blue = inputs and data. Black = formulas. Green = linked from another cell block. Yellow = placeholder the county should set. Change any blue cell and every budget updates.
1. Generator types (one site = one 100 kW setup)
Type | Cost per site ($) | Fuel | Fuel use per hour, full load | Fuel unit | Fuel price ($ per unit) | Fuel cost per day, per site ($) | Rental per week, per site ($) | What it is, source and notes
Hookup only (rent a generator in an outage) | 10000 | Diesel (rented unit) | 7.4 | gallons | 6.179 | 1097.3904 | 1569 | Electrician installs a quick connect box so a rented trailer generator can plug in. Cost: NJ Office of Emergency Management, HMGP permissible uses list: quick connect or tap box about $100 per kW (x 100 kW). Rental: Vandalia Rental, 100 kW generator, $1,569 per week ($640 per day, $4,035 per month). Fuel: same as diesel row.
Permanent generator, diesel | 58333 | Diesel | 7.4 | gallons | 6.179 | 1097.3904 | - | Built-in generator with a fuel tank on site. Needs fuel deliveries in a long outage. Cost: NC Dept. of Public Safety, June 2019: more than $1.4 million for 24 generators (22 to 500 kW), about $58,333 each. 2019 dollars. NJ OEM range for a permanent generator: $450 to $650 per kW ($45,000 to $65,000 at 100 kW). Fuel: Herc Rentals, 100 kW at full load = 7.4 gal per hour. Price: EIA U.S. diesel retail, week of Oct 12, 2026.
Permanent generator, natural gas | 104643.75 | Natural gas | 1374 | cubic feet | 0.01303 | 429.6773 | - | Built-in generator on the gas line. No fuel deliveries, but only where piped gas exists. Cost: average cost per kW of two 2026 quotes, times kW per site: Santa Fe, TX, 40 kW gas unit for Runge Park Community Center, $39,465 (May 2026); Stow, OH, 80 kW natural gas unit for the community center, $88,500 (Aug 2026). Fuel: Generac QT100 manual, 1,374 cubic feet per hour at full load. Price: EIA U.S. commercial natural gas, July 2026, $13.03 per 1,000 cubic feet. The diesel cost above is in 2019 dollars, so part of the gap is price growth, not fuel type.
Solar panels plus battery | 589147 | Sun | 0 | none | 0 | 0 | - | Solar on the roof and a battery. No fuel, but less power than a 100 kW generator. Cost: Oregon Dept. of Energy grant, Feb 2026: Silver Falls Library District, 71 kW solar and 240 kWh battery, $589,147, so the library can act as an emergency center in outages. This is a grant amount; the full project cost may be higher. Best for critical loads only.
2. Other inputs
Input | Value | Source and notes
FEMA share of cost | 75% | FEMA Hazard Mitigation Grant Program share in the NC 2019 program (state paid 25%). Varies by program.
Expected turnout at sites | 25% | PLACEHOLDER, not sourced. Share of people who would come to a site in a long outage. The county should set this.
Power per person, low (watts) | 275 | Inogen At Home oxygen concentrator at 5 liters per minute (Inogen energy calculator).
Power per person, high (watts) | 550 | Inogen says many concentrators use more than twice 275 W.
Reach, rural (miles) | 10 | Assumption. Straight-line distance used by the rural site picker.
Reach, urban (miles) | 3 | Assumption. People without a car can't travel far. Urban site counts come from power needs.
Days in a long outage | 3 | PLANNING ASSUMPTION for the fuel and rental columns. Hurricane Beryl left 1.1 million Houston-area customers out 3 days later (Axios, Jul 11, 2024).
Power per site (kW) | 100 | PLANNING ASSUMPTION, not sourced. One generator at a typical small public building. NC program sizes ranged 22 to 500 kW.
3. County plans | [15 empty] | Cost for recommended sites, by generator type |  |  |  | Cost for the high estimate, by generator type |  |  |  |  | Running cost, recommended sites
County | State | FIPS | Type | Population (2020) | Medicare members | Rely on powered equipment | Share of Medicare members | Reach (mi) | Expected at sites | Power needed, low (kW) | Power needed, high (kW) | Sites from map (rural) | Sites for full map coverage (rural) | Recommended sites | Sites, high estimate | Hookups only ($) | Diesel ($) | Natural gas ($) | Solar + battery ($) | Hookups only, high ($) | Diesel, high ($) | Natural gas, high ($) | Solar + battery, high ($) | Local share if FEMA pays, diesel ($) | Hookups: rent for a long outage ($) | Diesel fuel for a long outage ($) | Natural gas for a long outage ($) | People in ZIP data (rural) | People reached, recommended sites (rural) | Coverage, recommended sites | How sites were counted
Los Angeles County | CA | 06037 | Urban | 10014009 | 1716142 | 67311 | 3.922% | 3 | 16827.75 | 4627.6313 | 9255.2625 |  |  | 47 | 93 | 470000 | 2741651 | 4918256.25 | 27689909 | 930000 | 5424969 | 9731868.75 | 54790671 | 685412.75 | 228475.0464 | 154732.0464 | 60584.4965 |  |  | See Urban Site Plans | Power needs: expected people x watts / kW per site
Cook County | IL | 17031 | Urban | 5275541 | 880036 | 33574 | 3.815% | 3 | 8393.5 | 2308.2125 | 4616.425 |  |  | 24 | 47 | 240000 | 1399992 | 2511450 | 14139528 | 470000 | 2741651 | 4918256.25 | 27689909 | 349998 | 116668.1088 | 79012.1088 | 30936.7642 |  |  | See Urban Site Plans | Power needs: expected people x watts / kW per site
Harris County | TX | 48201 | Urban | 4731145 | 672080 | 28811 | 4.287% | 3 | 7202.75 | 1980.7562 | 3961.5125 |  |  | 20 | 40 | 200000 | 1166660 | 2092875 | 11782940 | 400000 | 2333320 | 4185750 | 23565880 | 291665 | 97223.424 | 65843.424 | 25780.6368 |  |  | See Urban Site Plans | Power needs: expected people x watts / kW per site
Maricopa County | AZ | 04013 | Urban | 4420568 | 817022 | 32883 | 4.025% | 3 | 8220.75 | 2260.7063 | 4521.4125 |  |  | 23 | 46 | 230000 | 1341659 | 2406806.25 | 13550381 | 460000 | 2683318 | 4813612.5 | 27100762 | 335414.75 | 111806.9376 | 75719.9376 | 29647.7323 |  |  | See Urban Site Plans | Power needs: expected people x watts / kW per site
Miami-Dade County | FL | 12086 | Urban | 2701767 | 525034 | 23346 | 4.447% | 3 | 5836.5 | 1605.0375 | 3210.075 |  |  | 17 | 33 | 170000 | 991661 | 1778943.75 | 10015499 | 330000 | 1924989 | 3453243.75 | 19441851 | 247915.25 | 82639.9104 | 55966.9104 | 21913.5413 |  |  | See Urban Site Plans | Power needs: expected people x watts / kW per site
Athens County | OH | 39009 | Rural | 62431 | 12713 | 845 | 6.647% | 10 | 211.25 | 58.0938 | 116.1875 | 3 | 4 | 3 | 4 | 30000 | 174999 | 313931.25 | 1767441 | 40000 | 233332 | 418575 | 2356588 | 43749.75 | 14583.5136 | 9876.5136 | 3867.0955 | 829 | 805 | 97.1% | Site picker on 7 real library branches, 10 mi. Full coverage adds a site near Amesville.
Harlan County | KY | 21095 | Rural | 26831 | 6953 | 875 | 12.58% | 10 | 218.75 | 60.1562 | 120.3125 | 2 | 4 | 2 | 4 | 20000 | 116666 | 209287.5 | 1178294 | 40000 | 233332 | 418575 | 2356588 | 29166.5 | 9722.3424 | 6584.3424 | 2578.0637 | 861 | 833 | 96.75% | Site picker on ZIP code centers (town centers), 10 mi
Coos County | NH | 33007 | Rural | 31268 | 11023 | 466 | 4.228% | 10 | 116.5 | 32.0375 | 64.075 | 5 | 8 | 5 | 8 | 50000 | 291665 | 523218.75 | 2945735 | 80000 | 466664 | 837150 | 4713176 | 72916.25 | 24305.856 | 16460.856 | 6445.1592 | 477 | 438 | 91.82% | Site picker on ZIP code centers (town centers), 10 mi
Big Horn County | MT | 30003 | Rural | 13124 | 2101 | 223 | 10.61% | 10 | 55.75 | 15.3313 | 30.6625 | 8 | 10 | 8 | 10 | 80000 | 466664 | 837150 | 4713176 | 100000 | 583330 | 1046437.5 | 5891470 | 116666 | 38889.3696 | 26337.3696 | 10312.2547 | 223 | 201 | 90.13% | Site picker on ZIP code centers (town centers), 10 mi
Sunflower County | MS | 28133 | Rural | 25971 | 4842 | 359 | 7.414% | 10 | 89.75 | 24.6812 | 49.3625 | 3 | 4 | 3 | 4 | 30000 | 174999 | 313931.25 | 1767441 | 40000 | 233332 | 418575 | 2356588 | 43749.75 | 14583.5136 | 9876.5136 | 3867.0955 | 359 | 345 | 96.1% | Site picker on ZIP code centers (town centers), 10 mi
Urban total |  |  |  | 27143030 |  | 185925 | [7 empty] | 131 | 259 | 1310000 | 7641623 | 13708331.25 | 77178257 | 2590000 | 15108247 | 27102731.25 | 152589073 | 1910405.75 | 636813.4272 | 431274.4272 | 168863.171
Rural total |  |  |  | 159625 |  | 2768 | [7 empty] | 21 | 30 | 210000 | 1224993 | 2197518.75 | 12372087 | 300000 | 1749990 | 3139312.5 | 17674410 | 306248.25 | 102084.5952 | 69135.5952 | 27069.6686
All 10 counties |  |  |  | 27302655 |  | 188693 | [7 empty] | 152 | 289 | 1520000 | 8866616 | 15905850 | 89550344 | 2890000 | 16858237 | 30242043.75 | 170263483 | 2216654 | 738898.0224 | 500410.0224 | 195932.8397
How to read this sheet
Recommended sites: rural = the larger of (sites to reach at least 90% of people in the ZIP data, from the site picker) and (sites needed for power at the high wattage). Urban = sites for power at the low wattage.
Sites, high estimate: rural = sites to reach everyone in the ZIP data. Urban = sites for power at the high wattage.
Each budget = number of sites x cost per site for that generator type (block 1). Running costs = sites x cost per day x days in a long outage (block 2).
Hookups are the cheapest to set up but the county pays rent and fuel every outage. Natural gas needs no fuel deliveries but only works where there is a gas line, which many rural areas lack.
Solar + battery has no fuel cost but gives less power than a 100 kW generator, so it suits critical loads (oxygen, medicine fridge, phone charging).
People counts are Medicare members only (HHS emPOWER, county layer, updated Aug 2026). ZIP data hides counts of 1 to 10 as 11, so ZIP totals can differ from county totals.
Costs are planning estimates from public records and price lists, not quotes. Regional price differences are not included.
Sources
HHS emPOWER REST Service (county and ZIP layers): https://services2.arcgis.com/ZQ4jTQn6k7VPXEwO/ArcGIS/rest/services/HHS_emPOWER_REST_Service_Public/FeatureServer
2020 Census population: Wikipedia county pages (U.S. Census Bureau figures)
NJ Office of Emergency Management, HMGP permissible uses list: https://nj.gov/njoem/programs/pdf/hmgp/062414_hmgp_permlist.pdf
NC Department of Public Safety, June 18, 2019: https://ncdps.gov/news/press-releases/2019/06/18/communities-receive-generators-powering-critical-public
City of Santa Fe, TX, council packet with Runge Park generator quote, May 2026: https://www.santafetx.gov/media/17821
Stow, OH, community center generator, Aug 6, 2026 (Citizen Portal meeting summary): https://citizenportal.ai/articles/10770385/ohio/summit-county/stow-city/committee-amends-generator-funding-line-and-advances-community-center-generator-to-council
Oregon Department of Energy, community energy grants, Feb 5, 2026: https://energyinfo.oregon.gov/blog/2026/2/5/oregon-department-of-energy-grants-support-renewable-and-resilient-energy-development-from-canyonville-to-cascade-locks
Vandalia Rental, 100 kW generator rates: https://vandaliarental.com/equipment/generator-100-kw-3-phase/
Herc Rentals, diesel generator fuel use: https://blog.hercrentals.com/power-generation/how-to-calculate-diesel-generator-fuel-consumption/
Generac QT100 (QT10054GNSN) manual, fuel table: https://www.notice-facile.com/en/manual/1523359/generac+qt10054gnsn
EIA diesel retail price, week of Oct 12, 2026: https://www.eia.gov/petroleum/gasdiesel/
EIA commercial natural gas price, July 2026: https://www.eia.gov/dnav/ng/hist/n3020us3m.htm
Inogen At Home energy calculator: https://www.inogen.com/products/energy-savings-calculator/
Axios Houston, Jul 11, 2024 (Beryl outage length): https://www.axios.com/local/houston/2024/07/11/houston-power-outage-storm-beryl-centerpoint

## Rural Site Plans
Rural site plans from the site picker
Each row adds the site that reaches the most people not yet covered (10 mile straight-line reach). Best possible = every combination checked, up to 6 sites. Cost columns = total for all sites so far.
County | Site # | Site | ZIP | New people reached | Total reached | People in ZIP data | Share reached | Best possible with this many | Site picker vs best | Hookups only ($) | Diesel ($) | Natural gas ($) | Solar + battery ($)
Athens County, OH | 1 | Chauncey Public Library | 45719 | 597 | 597 | 829 | 72.01% | 597 | 100% | 10000 | 58333 | 104643.75 | 589147
Athens County, OH | 2 | Coolville Public Library | 45723 | 107 | 704 | 829 | 84.92% | 704 | 100% | 20000 | 116666 | 209287.5 | 1178294
Athens County, OH | 3 | Wells (Albany) Public Library | 45710 | 101 | 805 | 829 | 97.1% | 805 | 100% | 30000 | 174999 | 313931.25 | 1767441
Harlan County, KY | 1 | Public building near Coalgood | 40818 | 638 | 638 | 861 | 74.1% | 638 | 100% | 10000 | 58333 | 104643.75 | 589147
Harlan County, KY | 2 | Public building near Lynch | 40855 | 195 | 833 | 861 | 96.75% | 833 | 100% | 20000 | 116666 | 209287.5 | 1178294
Harlan County, KY | 3 | Public building near Coldiron | 40819 | 17 | 850 | 861 | 98.72% | 861 | 98.72% | 30000 | 174999 | 313931.25 | 1767441
Harlan County, KY | 4 | Public building near Big Laurel | 40808 | 11 | 861 | 861 | 100% | 861 | 100% | 40000 | 233332 | 418575 | 2356588
Coos County, NH | 1 | Public building near Berlin | 03570 | 224 | 224 | 477 | 46.96% | 224 | 100% | 10000 | 58333 | 104643.75 | 589147
Coos County, NH | 2 | Public building near Lancaster | 03584 | 122 | 346 | 477 | 72.54% | 346 | 100% | 20000 | 116666 | 209287.5 | 1178294
Coos County, NH | 3 | Public building near Colebrook | 03576 | 47 | 393 | 477 | 82.39% | 393 | 100% | 30000 | 174999 | 313931.25 | 1767441
Coos County, NH | 4 | Public building near Twin Mountain | 03595 | 27 | 420 | 477 | 88.05% | 437 | 96.11% | 40000 | 233332 | 418575 | 2356588
Coos County, NH | 5 | Public building near Pittsburg | 03592 | 18 | 438 | 477 | 91.82% | 455 | 96.26% | 50000 | 291665 | 523218.75 | 2945735
Coos County, NH | 6 | Public building near Groveton | 03582 | 17 | 455 | 477 | 95.39% | 466 | 97.64% | 60000 | 349998 | 627862.5 | 3534882
Coos County, NH | 7 | Public building near Errol | 03579 | 11 | 466 | 477 | 97.69% | Not checked |  | 70000 | 408331 | 732506.25 | 4124029
Coos County, NH | 8 | Public building near Jackson | 03846 | 11 | 477 | 477 | 100% | Not checked |  | 80000 | 466664 | 837150 | 4713176
Big Horn County, MT | 1 | Public building near Hardin | 59034 | 93 | 93 | 223 | 41.7% | 93 | 100% | 10000 | 58333 | 104643.75 | 589147
Big Horn County, MT | 2 | Public building near Crow Agency | 59022 | 32 | 125 | 223 | 56.05% | 125 | 100% | 20000 | 116666 | 209287.5 | 1178294
Big Horn County, MT | 3 | Public building near Lodge Grass | 59050 | 20 | 145 | 223 | 65.02% | 145 | 100% | 30000 | 174999 | 313931.25 | 1767441
Big Horn County, MT | 4 | Public building near Busby | 59016 | 12 | 157 | 223 | 70.4% | 157 | 100% | 40000 | 233332 | 418575 | 2356588
Big Horn County, MT | 5 | Public building near Pryor | 59066 | 11 | 168 | 223 | 75.34% | 168 | 100% | 50000 | 291665 | 523218.75 | 2945735
Big Horn County, MT | 6 | Public building near Garryowen | 59031 | 11 | 179 | 223 | 80.27% | 179 | 100% | 60000 | 349998 | 627862.5 | 3534882
Big Horn County, MT | 7 | Public building near Fort Smith | 59035 | 11 | 190 | 223 | 85.2% | Not checked |  | 70000 | 408331 | 732506.25 | 4124029
Big Horn County, MT | 8 | Public building near Saint Xavier | 59075 | 11 | 201 | 223 | 90.13% | Not checked |  | 80000 | 466664 | 837150 | 4713176
Big Horn County, MT | 9 | Public building near Wyola | 59089 | 11 | 212 | 223 | 95.07% | Not checked |  | 90000 | 524997 | 941793.75 | 5302323
Big Horn County, MT | 10 | Public building near Decker | 59025 | 11 | 223 | 223 | 100% | Not checked |  | 100000 | 583330 | 1046437.5 | 5891470
Sunflower County, MS | 1 | Public building near Sunflower | 38778 | 250 | 250 | 359 | 69.64% | 250 | 100% | 10000 | 58333 | 104643.75 | 589147
Sunflower County, MS | 2 | Public building near Doddsville | 38736 | 53 | 303 | 359 | 84.4% | 303 | 100% | 20000 | 116666 | 209287.5 | 1178294
Sunflower County, MS | 3 | Public building near Drew | 38737 | 42 | 345 | 359 | 96.1% | 345 | 100% | 30000 | 174999 | 313931.25 | 1767441
Sunflower County, MS | 4 | Public building near Inverness | 38753 | 14 | 359 | 359 | 100% | 359 | 100% | 40000 | 233332 | 418575 | 2356588
Athens sites are real library branches (Athens County Public Libraries, myacpl.org), placed at their ZIP center. Amesville (ZIP 45711, 24 people) is not within 10 miles of any library.
Sites for Harlan, Coos, Big Horn and Sunflower are town centers (ZIP code centers), not specific buildings yet.
Costs per site come from block 1 on the County Plans sheet.

## Urban Site Plans
Urban site plans: start with the 10 ZIP codes that have the most people at risk
Big counties are planned one area at a time. Each row sizes the sites for one ZIP code from its power needs (people x turnout x watts / kW per site). Pick a library, school, or community center inside each ZIP.
County | Rank | ZIP | Area | Rely on powered equipment | Share of county total | Expected at sites | Power needed, low (kW) | Power needed, high (kW) | Sites needed | Sites, high estimate | Hookups only ($) | Diesel ($) | Natural gas ($) | Solar + battery ($)
Los Angeles County, CA | 1 | 93535 | Lancaster | 824 | 1.224% | 206 | 56.65 | 113.3 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 2 | 93536 | Lancaster | 771 | 1.145% | 192.75 | 53.0063 | 106.0125 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 3 | 90650 | Norwalk | 723 | 1.074% | 180.75 | 49.7062 | 99.4125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 4 | 91342 | Sylmar | 700 | 1.04% | 175 | 48.125 | 96.25 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 5 | 93550 | Palmdale | 697 | 1.035% | 174.25 | 47.9188 | 95.8375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 6 | 93534 | Lancaster | 678 | 1.007% | 169.5 | 46.6125 | 93.225 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 7 | 91331 | Pacoima | 658 | 0.9776% | 164.5 | 45.2375 | 90.475 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 8 | 91335 | Reseda | 633 | 0.9404% | 158.25 | 43.5187 | 87.0375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 9 | 90044 | Los Angeles | 620 | 0.9211% | 155 | 42.625 | 85.25 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA | 10 | 91744 | La Puente | 581 | 0.8632% | 145.25 | 39.9438 | 79.8875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Los Angeles County, CA: top 10 ZIPs |  |  |  | 6885 | 10.23% | 1721.25 | 473.3438 | 946.6875 | 10 | 12 | 100000 | 583330 | 1046437.5 | 5891470
Cook County, IL | 1 | 60620 | Chicago | 755 | 2.249% | 188.75 | 51.9062 | 103.8125 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 2 | 60617 | Chicago | 724 | 2.156% | 181 | 49.775 | 99.55 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 3 | 60628 | Chicago | 712 | 2.121% | 178 | 48.95 | 97.9 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 4 | 60619 | Chicago | 661 | 1.969% | 165.25 | 45.4438 | 90.8875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 5 | 60411 | Chicago Heights | 558 | 1.662% | 139.5 | 38.3625 | 76.725 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 6 | 60643 | Chicago | 527 | 1.57% | 131.75 | 36.2313 | 72.4625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 7 | 60453 | Oak Lawn | 517 | 1.54% | 129.25 | 35.5438 | 71.0875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 8 | 60629 | Chicago | 502 | 1.495% | 125.5 | 34.5125 | 69.025 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 9 | 60409 | Calumet City | 423 | 1.26% | 105.75 | 29.0813 | 58.1625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL | 10 | 60634 | Chicago | 415 | 1.236% | 103.75 | 28.5312 | 57.0625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Cook County, IL: top 10 ZIPs |  |  |  | 5794 | 17.26% | 1448.5 | 398.3375 | 796.675 | 10 | 11 | 100000 | 583330 | 1046437.5 | 5891470
Harris County, TX | 1 | 77449 | Katy | 648 | 2.249% | 162 | 44.55 | 89.1 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 2 | 77379 | Spring | 577 | 2.003% | 144.25 | 39.6688 | 79.3375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 3 | 77084 | Houston | 563 | 1.954% | 140.75 | 38.7062 | 77.4125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 4 | 77521 | Baytown | 531 | 1.843% | 132.75 | 36.5063 | 73.0125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 5 | 77429 | Cypress | 530 | 1.84% | 132.5 | 36.4375 | 72.875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 6 | 77433 | Cypress | 524 | 1.819% | 131 | 36.025 | 72.05 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 7 | 77088 | Houston | 453 | 1.572% | 113.25 | 31.1438 | 62.2875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 8 | 77346 | Humble | 451 | 1.565% | 112.75 | 31.0063 | 62.0125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 9 | 77083 | Houston | 435 | 1.51% | 108.75 | 29.9062 | 59.8125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX | 10 | 77095 | Houston | 413 | 1.433% | 103.25 | 28.3938 | 56.7875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Harris County, TX: top 10 ZIPs |  |  |  | 5125 | 17.79% | 1281.25 | 352.3438 | 704.6875 | 10 | 10 | 100000 | 583330 | 1046437.5 | 5891470
Maricopa County, AZ | 1 | 85351 | Sun City | 901 | 2.74% | 225.25 | 61.9438 | 123.8875 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 2 | 85375 | Sun City West | 784 | 2.384% | 196 | 53.9 | 107.8 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 3 | 85374 | Surprise | 689 | 2.095% | 172.25 | 47.3687 | 94.7375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 4 | 85345 | Peoria | 569 | 1.73% | 142.25 | 39.1187 | 78.2375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 5 | 85308 | Glendale | 533 | 1.621% | 133.25 | 36.6437 | 73.2875 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 6 | 85205 | Mesa | 514 | 1.563% | 128.5 | 35.3375 | 70.675 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 7 | 85248 | Chandler | 510 | 1.551% | 127.5 | 35.0625 | 70.125 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 8 | 85382 | Peoria | 484 | 1.472% | 121 | 33.275 | 66.55 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 9 | 85326 | Buckeye | 482 | 1.466% | 120.5 | 33.1375 | 66.275 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ | 10 | 85206 | Mesa | 479 | 1.457% | 119.75 | 32.9312 | 65.8625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Maricopa County, AZ: top 10 ZIPs |  |  |  | 5945 | 18.08% | 1486.25 | 408.7188 | 817.4375 | 10 | 12 | 100000 | 583330 | 1046437.5 | 5891470
Miami-Dade County, FL | 1 | 33012 | Hialeah | 909 | 3.894% | 227.25 | 62.4937 | 124.9875 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 2 | 33157 | Miami | 748 | 3.204% | 187 | 51.425 | 102.85 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 3 | 33165 | Miami | 739 | 3.165% | 184.75 | 50.8062 | 101.6125 | 1 | 2 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 4 | 33175 | Miami | 665 | 2.848% | 166.25 | 45.7188 | 91.4375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 5 | 33142 | Miami | 623 | 2.669% | 155.75 | 42.8312 | 85.6625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 6 | 33186 | Miami | 582 | 2.493% | 145.5 | 40.0125 | 80.025 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 7 | 33125 | Miami | 569 | 2.437% | 142.25 | 39.1187 | 78.2375 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 8 | 33010 | Hialeah | 562 | 2.407% | 140.5 | 38.6375 | 77.275 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 9 | 33155 | Miami | 550 | 2.356% | 137.5 | 37.8125 | 75.625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL | 10 | 33176 | Miami | 527 | 2.257% | 131.75 | 36.2313 | 72.4625 | 1 | 1 | 10000 | 58333 | 104643.75 | 589147
Miami-Dade County, FL: top 10 ZIPs |  |  |  | 6474 | 27.73% | 1618.5 | 445.0875 | 890.175 | 10 | 13 | 100000 | 583330 | 1046437.5 | 5891470
ZIP counts: HHS emPOWER ZIP layer, updated Aug 2026, pulled Oct 17, 2026. Medicare members only.
Share of county total compares each ZIP with the county-layer total, so shares can be a little off (ZIP data rounds small counts up to 11).
Sites per ZIP round up, so the top-10 total can be higher than the same people would need in the county-wide count.
Next step for each ZIP: pick a public building (library, school, fire station) and confirm it has room and a safe spot for a generator.